| Up time | .1.3.6.1.2.1.1.3.0 | TimeTicks |
| --- | --- | --- |
| Sys Contact | .1.3.6.1.2.1.1.4.0 | OctetString |
| Sys Name | .1.3.6.1.2.1.1.5.0 | OctetString |
| Sys Location | .1.3.6.1.2.1.1.6.0 | OctetString |
| Line A status | .1.3.6.1.4.1.5491.5.1.2.5.1.0 | 0 for line OK, 1 for black-out |
| BATTERY |  |  |
| rupsBatteryStatus | .1.3.6.1.4.1.5491.10.1.2.1 | INTEGER {unknown(1),batteryNormal(2),batteryLow(3),batteryDepleted(4)} The indication of the capacity remaining in the UPS system's batteries. A value of batteryNormal indicates that the remaining run-time is greater than rupsConfigLowBattTime. A value of batteryLow indicates that the remaining battery run-time is less than or equal to rupsConfigLowBattTime. A value of batteryDepleted indicates that the UPS will be unable to sustain the present load when and if the utility power is lost (including the possibility that the utility power is currently absent and the UPS is unable to sustain the output). |
| rupsSecondsOnBattery | .1.3.6.1.4.1.5491.10.1.2.2.0 | If the unit is on battery power, the elapsed time since the UPS last switched to battery power, or the time since the network management subsystem was last restarted, whichever is less. Zero shall be returned if the unit is not on battery power. |
| rupsEstimatedMinutesRemaining | .1.3.6.1.4.1.5491.10.1.2.3.0 | An estimate of the time to battery charge depletion under the present load conditions if the utility power is off and remains off, or if it were to be lost and remain off. |
| rupsEstimatedChargeRemaining | .1.3.6.1.4.1.5491.10.1.2.4.0 | An estimate of the battery charge remaining expressed as a percent of full charge. (100 no remaining) |
| rupsBatteryVoltage | .1.3.6.1.4.1.5491.10.1.2.5.0 | The magnitude of the present battery voltage. / 10 |
| rupsBatteryCurrent | .1.3.6.1.4.1.5491.10.1.2.6.0 | The present battery current. (-1 no data) |
| rupsBatteryTemperature | .1.3.6.1.4.1.5491.10.1.2.7.0 | The ambient temperature at or near the UPS Battery casing. |
| .1.3.6.1.4.1.5491.10.1.2.12.0 |  | The charging/discharging status of the battery INTEGER {discharging(0), charging(1)} |

Manufacturer : .1.3.6.1.4.1.5491.10.1.1.1.0

.1.3.6.1.4.1.5491.10.1.1.3.0

.1.3.6.1.4.1.5491.10.1.1.12.0

.1.3.6.1.4.1.5491.10.1.1.9.0 / 1000

.1.3.6.1.4.1.5491.10.1.1.10.0 / 1000

.1.3.6.1.4.1.5491.10.1.1.11.0

.1.3.6.1.4.1.5491.10.1.1.2.0

.1.3.6.1.4.1.5491.10.1.1.4.0

.1.3.6.1.4.1.5491.5.1.1.8.0

BYPASS POWER, CURRENT  > 0

INPUT VOLTAGE > 0

.1.3.6.1.4.1.5491.10.1.2.4.0

OUTPUT LOAD

OUTPUT CURRENT >0

.1.3.6.1.4.1.5491.10.1.4.1.0

INTEGER {other(1),none(2),normal(3),bypass(4),battery(5),booster(6),

reducer(7)}

The present source of output power.  The enumeration

none(2) indicates that there is no source of output

power (and therefore no output power), for example,

the system has opened the output breaker.

.1.3.6.1.4.1.5491.10.1.4.4.1.5 (3)

.1.3.6.1.4.1.5491.10.1.4.4.1.6 (3)

PEAK CURRENT (W)

POWER (W)

.1.3.6.1.4.1.5491.10.1.4.4.1.4 (3)

.1.3.6.1.4.1.5491.10.1.4.4.1.3 (3)

.1.3.6.1.4.1.5491.10.1.4.4.1.2 (3)

.1.3.6.1.4.1.5491.10.1.4.2.0

.1.3.6.1.4.1.5491.10.1.3.3.1.5 (3)

POWER (W)

.1.3.6.1.4.1.5491.10.1.3.3.1.4 (3)

.1.3.6.1.4.1.5491.10.1.3.3.1.3 (3)

.1.3.6.1.4.1.5491.10.1.3.3.1.2.1

POWER (W)

.1.3.6.1.4.1.5491.10.1.5.3.1.4 (3)

.1.3.6.1.4.1.5491.10.1.5.1.0

.1.3.6.1.4.1.5491.10.1.5.3.1.3 (3)

.1.3.6.1.4.1.5491.10.1.5.3.1.2 (3)

.1.3.6.1.4.1.5491.10.1.2.3.0

-1  = “-“

.1.3.6.1.4.1.5491.12.2.16.0

.1.3.6.1.4.1.5491.10.1.2.5.0 / 10

.1.3.6.1.4.1.5491.10.1.2.4.0