## Hoja1
GENERAL
Up time |  | .1.3.6.1.2.1.1.3.0 | TimeTicks
Sys Contact |  | .1.3.6.1.2.1.1.4.0 | OctetString
Sys Name |  | .1.3.6.1.2.1.1.5.0 | OctetString
Sys Location |  | .1.3.6.1.2.1.1.6.0 | OctetString
Line A status |  | .1.3.6.1.4.1.5491.5.1.2.5.1.0 | Integer | 0 for line OK, 1 for black-out
Model |  | .1.3.6.1.4.1.5491.10.1.1.2.0 | OctetString
Power ampers | VA | .1.3.6.1.4.1.5491.10.1.1.9.0 | Integer | Not available : -1
Power watts | W | .1.3.6.1.4.1.5491.10.1.1.10.0 | Integer | Not available : -1
Battery capacity | Ah | .1.3.6.1.4.1.5491.10.1.1.12.0 | Integer | Not available : -1
Battery voltage | Vdc | .1.3.6.1.4.1.5491.10.1.1.11.0 | Integer | Not available : -1
Firmware version |  | .1.3.6.1.4.1.5491.10.1.1.3.0 | OctetString
Application version |  | .1.3.6.1.4.1.5491.10.1.1.4.0 | OctetString
System temperature | ºC | .1.3.6.1.4.1.5491.10.1.10.1.0 | Integer
INPUT
Input voltage L1 | V | .1.3.6.1.4.1.5491.10.1.3.3.1.3.1 | Integer | Not available : -1
Input current L1 | A | .1.3.6.1.4.1.5491.10.1.3.3.1.4.1 | Integer | Not available : -1
Input true power L1 | W | .1.3.6.1.4.1.5491.10.1.3.3.1.5.1 | Integer | Not available : -1
Input frequency L1 | Hz * 10 | .1.3.6.1.4.1.5491.10.1.3.3.1.2.1 | Integer | Not available : -1
OUTPUT
Output source |  |  |  | The present source of output power. The enumeration none(2) indicates that there is no source of output power (and therefore no output power), for example, the system has opened the output breaker. {other(1),none(2),normal(3),bypass(4),battery(5),booster(6),reducer(7)}
Output frequency L1 | Hz * 10 | .1.3.6.1.4.1.5491.10.1.4.2.0 | Integer | Not available : -1
Output voltage L1 | V | .1.3.6.1.4.1.5491.10.1.4.4.1.2.1 | Integer | Not available : -1
Output current L1 | A | .1.3.6.1.4.1.5491.10.1.4.4.1.3.1 | Integer | Not available : -1
Output power L1 | W | .1.3.6.1.4.1.5491.10.1.4.4.1.4.1 | Integer | Not available : -1
Output load L1 | % | .1.3.6.1.4.1.5491.10.1.4.4.1.5.1 | Integer | Not available : -1
Output peak current L1 | A | .1.3.6.1.4.1.5491.10.1.4.4.1.6.1 | Integer | Not available : -1
BYPASS
Bypass frequency L1 | Hz * 10 | .1.3.6.1.4.1.5491.10.1.5.1.0 | Integer | Not available : -1
Bypass voltage L1 | V | .1.3.6.1.4.1.5491.10.1.5.3.1.2.1 | Integer | Not available : -1
Bypass current L1 | A | .1.3.6.1.4.1.5491.10.1.5.3.1.3.1 | Integer | Not available : -1
Bypass power L1 | W | .1.3.6.1.4.1.5491.10.1.5.3.1.4.1 | Integer | Not available : -1
BATTERY
rupsBatteryStatus |  | .1.3.6.1.4.1.5491.10.1.2.1 | Integer | {unknown(1),batteryNormal(2),batteryLow(3),batteryDepleted(4)} The indication of the capacity remaining in the UPS system's batteries. A value of batteryNormal indicates that the remaining run-time is greater than rupsConfigLowBattTime. A value of batteryLow indicates that the remaining battery run-time is less than or equal to rupsConfigLowBattTime. A value of batteryDepleted indicates that the UPS will be unable to sustain the present load when and if the utility power is lost (including the possibility that the utility power is currently absent and the UPS is unable to sustain the output).
rupsSecondsOnBattery |  | .1.3.6.1.4.1.5491.10.1.2.2.0 | Integer | If the unit is on battery power, the elapsed time since the UPS last switched to battery power, or the time since the network management subsystem was last restarted, whichever is less. Zero shall be returned if the unit is not on battery power.
rupsEstimatedMinutesRemaining |  | .1.3.6.1.4.1.5491.10.1.2.3.0 | Integer | An estimate of the time to battery charge depletion under the present load conditions if the utility power is off and remains off, or if it were to be lost and remain off.
rupsEstimatedChargeRemaining | % | .1.3.6.1.4.1.5491.10.1.2.4.0 | Integer | An estimate of the battery charge remaining expressed as a percent of full charge.
rupsBatteryVoltage | V * 10 | .1.3.6.1.4.1.5491.10.1.2.5.0 | Integer | The magnitude of the present battery voltage. / 10
rupsBatteryCurrent | A | .1.3.6.1.4.1.5491.10.1.2.6.0 | Integer | The present battery current. (-1 no data)
rupsBatteryTemperature | ºC | .1.3.6.1.4.1.5491.10.1.2.7.0 | Integer | The ambient temperature at or near the UPS Battery casing.
rupsIsCharging |  | .1.3.6.1.4.1.5491.10.1.2.12.0 | Integer | The charging/discharging status of the battery INTEGER {discharging(0), charging(1)}
TEST
Test results summary |  | .1.3.6.1.4.1.5491.10.1.7.3.0 | Integer | The results of the current or last UPS diagnostics test performed. The values for donePass(1), doneWarning(2), and doneError(3) indicate that the test completed either successfully, with a warning, or with an error, respectively. The value aborted(4) is returned for tests which are aborted by setting the value of upsTestId to upsTestAbortTestInProgress. Tests which have not yet concluded are indicated by inProgress(5). The value noTestsInitiated(6) indicates that no previous test results are available, such as is the case when no tests have been run since the last reinitialization of the network management subsystem and the system has no provision for non- volatile storage of test results.
Test results detail |  | .1.3.6.1.4.1.5491.10.1.7.4.0 | OctetString | Additional information about upsTestResultsSummary. If no additional information available, a zero length string is returned.
Test start time |  | .1.3.6.1.4.1.5491.10.1.7.5.0 | TimeTicks | The value of sysUpTime at the time the test in progress was initiated, or, if no test is in progress, the time the previous test was initiated. If the value of upsTestResultsSummary is noTestsInitiated(6), upsTestStartTime has the value 0.
Test elpased time |  | .1.3.6.1.4.1.5491.10.1.7.6.0 | TimeTicks | The amount of time, in TimeTicks, since the test in progress was initiated, or, if no test is in progress, the previous test took to complete. If the value of upsTestResultsSummary is noTestsInitiated(6), upsTestElapsedTime has the value 0.
ALARMS
Alarm battery bad |  | .1.3.6.1.4.1.5491.10.1.6.3.1 | TimeTicks? | Ojo que si no hay alarma el objeto no existe (NoSuchObject) The value of sysUpTime when the alarm condition was detected. If the alarm condition was detected at the time of agent startup and presumably existed before agent startup, the value of rupsAlarmTime shall equal 0.
Alarm on battery |  | .1.3.6.1.4.1.5491.10.1.6.3.2
Alarm low battery |  | .1.3.6.1.4.1.5491.10.1.6.3.3
Alarm shutdown inminent |  | .1.3.6.1.4.1.5491.10.1.6.3.4
Alarm temperature bad |  | .1.3.6.1.4.1.5491.10.1.6.3.5
Alarm fault |  | .1.3.6.1.4.1.5491.10.1.6.3.6
Alarm internal error |  | .1.3.6.1.4.1.5491.10.1.6.3.7
Alarm output overload |  | .1.3.6.1.4.1.5491.10.1.6.3.8
Alarm on bypass |  | .1.3.6.1.4.1.5491.10.1.6.3.9
Alarm bypass bad |  | .1.3.6.1.4.1.5491.10.1.6.3.10